## Slide 1: Portugal Cove - St. Philip’s
Water Metering Study
September 7, 2016

## Slide 2: Background
Treated Water Supplied by St. John’s Regional Water Authority
PCSP distributes Water to customers
PCSP collects and treats Wastewater
1,188 Residential and 20 Commercial Water Customers
1,064 Residential and 22 Commercial Wastewater Customers

## Slide 3: Current Charges
Water
  Residential - $475 water tax per year
  Commercial - $505 water tax per year
Wastewater
  Residential - $175 wastewater tax per year
  Commercial - $235 wastewater tax per year

## Slide 4: Water Consumption
Estimated Average Residential = 272 m3/year
Total Residential = (1,188 x 272) = 323,136 m3/year
Estimated Average Commercial = 2,720 m3/year
Total Commercial = (20 x 2,720) = 54,400 m3/year
Overall TOTAL = 377,536 m3/year

## Slide 5: Wastewater Volume
Actual Measured Flow = 417,980 m3/year

## Slide 6: Non-revenue Water
Purchase 810,000 m3 per year from Regional Water
Estimated Total water used by Customers = 377,536 m3/year
Non-revenue Water = 432,464 m3/year

## Slide 7: Water Purchased
Purchase 810,000 m3 per year @ $0.589/m3
Total Annual Cost of Water = (810,000 x $0.589)=$477,090

## Slide 8: Non-Revenue/Unaccounted for Water
Cost of water used by customers = $222,369
Cost of Non-revenue Water = $254,721

## Slide 9: Metering
Electronic or Mechanical Meters available
Both work well
Drive-By Reading Technology Recommended
Estimated Capital Cost = $1,500,000
Installation by Supplier Recommended

## Slide 10: Benefits
User Pay
Reduced Consumption (180 to 200 m3/year with meters)
Reduced Supply cost from Regional Water Authority
Improve water loss control
Reduced water loss control will result in reduced cost from the Regional Water Authority
Links Supply Cost to Revenue

## Slide 11: Benefits (cont’d)
Reduced Sewer System Loading
Customers have more control over their water bills
Reduces water demand on Regional Water System
Industry Recommended Practice by both AWWA and WEF

## Slide 12: Disadvantages
Revenue Security
Cost of Meters
Theft
Public Perception

## Slide 13: Future Rates and Charges
Recommend inclusion of a Base Charge for all customers based on meter size
Recommend inclusion of a Volumetric Charge for water used

## Slide 14: Cost Recovery from Rates
Currently not recovering full cost of operating the water system from the existing taxes

## Slide 15: Current Cost Recovery
Currently recovering direct costs
  Water Purchase
  Distribution System Operating Costs

## Slide 16
Name | No change in Non- revenue Water | 20% reduction in Non- Revenue Water | 50% reduction in Non- Revenue Water
Expenses |  |  | 
Administration and General | Not included | Not included | Not included
Transmission and Distribution | $327,910 | 327,910 | 327,910
Water Supply | $477,090 | 426,146 | 349,729
Current Debt Servicing Costs | Not included | Not included | Not included
Debt Payment for New Meters | $65,800 | $65,800 | $65,800
Replacement | Not included | Not included | Not included
Total | $870,800 | $819,856 | $743,439
Reduced costs from reduced consumption |  |  | 
consumption = 200 cm/year/customer | ($58,862) | ($58,862) | ($58,862)
Adjusted Total Budget | $811,938 | $760,994 | $684,577

## Slide 17
 | Base charge | Commodity charge | Total
No Change in Non-revenue Water | 193.17 | 263.24 | 456.40
20% reduction in Non- Revenue Water | 181.05 | 246.72 | 427.77
50% reduction in Non- Revenue Water | 162.87 | 221.95 | 384.81

## Slide 18: Findings
Water meters should be installed in all residential and commercial locations
Transition billing to a Base Charge and Consumption Charge
Initiate a comprehensive Water Loss Control Program

## Slide 19: Findings
Update By-laws
Direct savings from metering will be from reduced consumption
In-direct savings from metering will be from improved water loss control when used in concert with a Comprehensive Water Loss Program
Read meters for 1 year before switching the billing system